## Slide 1: POLCA – Characterization Summary
Training clusters: synchronized spikes (~3% headroom)
  Inference clusters: desynchronized workloads (~21% headroom)
  Cluster-level power smoother than per-server peaks
  Inference offers safe power oversubscription opportunity
  OOB GPU control is slow → requires proactive design

## Slide 2: From Characterization to Design
Exploit inference power headroom safely
  Maximize additional servers under fixed power budget
  Preserve inference latency SLOs
  Work under virtualization (no IB driver access)
  Integrate with existing datacenter power hierarchy

## Slide 3: POLCA Architecture Flow
Row Power Monitoring
(PDU + IPMI)
POLCA Controller
(Headroom + Risk Detection)
Throttle Decision
(SLO-aware selection)
OOB Command
(BMC → SMBPBI)
GPU Frequency Lock Applied

## Slide 4: POLCA Control Loop
1. Monitor row-level power continuously
  2. Compute headroom (Budget - Current Usage)
  3. Detect risk proactively (before violation)
  4. Select low-priority inference servers
  5. Apply GPU frequency locking via OOB
  6. Restore frequency when safe

## Slide 5: Why Frequency Locking?
Power capping is reactive and unstable
  Frequency locking gives predictable power reduction
  Reduces oscillations in cluster power
  Better SLO protection
  Works with slow OOB interfaces

## Slide 6: Implementation Outcome
Safe power oversubscription for inference clusters
  Supports ~30% more servers
  Minimal throttling events
  Minimal latency degradation
  Deployable using existing infrastructure